{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["A标段阀门","B标段补偿器"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"A标段阀门","index":0,"n_rows":27,"n_cols":13,"rows_kept":27,"merged":[[0,0,0,2],[1,0,1,13],[2,0,2,3],[20,1,20,3],[20,9,20,12],[21,0,21,9],[23,0,23,14],[24,0,24,14],[25,0,25,14],[26,0,26,3],[26,9,26,12]],"flags":["formulas_cached_only"]}
["附件3："]
["报 价 货 物 数 量 及 价 目 表"]
["比选编号：长招办询2024-003",{"$nulls":11},"A标段"]
["序号","物料代码","物料名称","规格/型号","技术要求","单位","数量","单价\n（元）","合计（元）","付款方式","交货期","报价货物品牌/厂家","备注"]
[1,null,"电子式电动调节切断蝶阀","DZWY 型 DN600 PN0.25Mpa 耐温：150℃","技术要求： 1）介质：转炉煤气，工作温度：80℃\n2）阀门采用三偏心金属硬密封结构，具有调节和切断功能;\n3）最大流量：11000Nm3/h，常用流量：9000Nm3/h 最小流量：0Nm3/h；阀前压力（10）±0.5kPa，阀后压力 8kPa；\n4）阀门启闭应灵活，电动时启闭时间不大于 60 秒；基本误差±1%，死区＜1.0%，回差＜1.0%，响应时间不大于 3s，失电阀门关闭；\n5）带智能一体化电动执行机构，执行机构带远程转换器，可就地和远程操作（带就地操作按钮），电压 AC380V，信号为 4-20mA;\n6）所处环境为工业大气环境，露天安装，位置属爆炸危险环境 2 区，电气设备需防爆，等级不低于 ExdII BT4；\n7）阀门接口管径为∅630X6，材质均为 Q235-B；\n8）煤气冷凝水中含有较高的 SO42- .CO32- .PO43-具有较高的腐蚀性，阀门须考虑相应的防腐措施。","台",1,{"$nulls":5},"第一批"]
[2,null,"电子式电动调节切断蝶阀","DZWY 型 DN1800 PN0.25Mpa 耐温：150℃","技术要求： 1）介质：高炉煤气，最高工作温度：100℃。\n2）阀门采用三偏心金属硬密封结构，具有调节和切断功能;\n3）最大流量：160000Nm3/h，常用流量：130000Nm3/h，最小流量：40000Nm3/h；阀前压力 10-12kPa，阀后压力 7.5-7.8kPa；\n4）阀门启闭应灵活，电动时启闭时间不大于 60 秒；基本误差±1%，死区＜1.0%，回差＜1.0%，响应时间不大于 3s，失电维持阀位；\n5）带智能一体化电动执行机构，执行机构带远程转换器，可就地和远程操作（带就地操作按钮），电压 AC380V，信号为 4-20mA;\n6）所处环境为工业大气环境，露天安装，位置处于爆炸危险环境 2 区，电气设备需防爆，等级不低于 ExdII BT4；\n7）阀门接口管径分别为∅1820x10，材质均为 Q235-B；\n8）煤气冷凝水中含有较高的SO42- .CO32- .Cl-，具有较高的腐蚀性，阀门须考虑相应的防腐措施。\n9）阀门带底座，阀中心距底座 1350mm。","台",1,{"$nulls":5},"第一批"]
[3,"S24037369","电动插板阀","F941X-2.5","PN0.25MPa DN1800，介质：高炉煤气，耐温：150℃，带波纹管，波纹管材质：316L\n带底座、配对法兰、螺栓、螺母及金属缠绕垫片\n带室外防爆电控箱，可实现 PLC 远传控制功能，预留 PLC 接口。","台",1,{"$nulls":5},"第二批"]
[4,"S24037370","电动金属硬密封蝶阀","D943PT-2.5","PN0.25MPa DN1800，介质：高炉煤气，耐温：150℃\n带底座、配对法兰、螺栓、螺母及金属缠绕垫片\n带室外防爆电控箱，可实现 PLC 远传控制功能，预留 PLC 接口。","台",1,{"$nulls":5},"第二批"]
[5,"S24037371","电动插板阀","F941X-2.5","PN0.25MPa DN1000，介质：焦炉煤气，耐温：150℃，带波纹管，波纹管材质：316L\n带底座、配对法兰、螺栓、螺母及金属缠绕垫片\n带室外防爆电控箱，可实现 PLC 远传控制功能，预留 PLC 接口。","台",1,{"$nulls":5},"第二批"]
[6,"S24037372","电动金属硬密封蝶阀","D943PT-2.5","PN0.25MPa DN1000，介质：焦炉煤气，耐温：150℃\n带底座、配对法兰、螺栓、螺母及金属缠绕垫片\n带室外防爆电控箱，可实现 PLC 远传控制功能，预留 PLC 接口。","台",1,{"$nulls":5},"第二批"]
[7,"S24037373","电动插板阀","F941X-2.5","PN0.25MPa DN600，介质：转炉煤气，耐温：150℃，带波纹管，波纹管材质：316L\n带底座、配对法兰、螺栓、螺母及金属缠绕垫片\n带室外防爆电控箱，可实现 PLC 远传控制功能，预留 PLC 接口。","台",1,{"$nulls":5},"第二批"]
[8,"S24037374","电动金属硬密封蝶阀","D943PT-2.5","PN0.25MPa DN600，介质：转炉煤气，耐温：150℃\n带底座、配对法兰、螺栓、螺母及金属缠绕垫片\n带室外防爆电控箱，可实现 PLC 远传控制功能，预留 PLC 接口。","台",1,{"$nulls":5},"第二批"]
[9,"S24037375","电动翻板阀","F943X-2.5","PN0.25MPa DN200，介质：焦炉煤气，耐温：150℃，带波纹管，波纹管材质：316L\n带底座、配对法兰、螺栓、螺母及金属缠绕垫片\n带室外防爆电控箱，可实现 PLC 远传控制功能，预留 PLC 接口。","台",1,{"$nulls":5},"第二批"]
[10,"S24037376","电动金属硬密封蝶阀","D943PT-2.5","PN0.25MPa DN200，介质：焦炉煤气，耐温：150℃\n带底座、配对法兰、螺栓、螺母及金属缠绕垫片\n带室外防爆电控箱，可实现 PLC 远传控制功能，预留 PLC 接口。","台",1,{"$nulls":5},"第二批"]
[11,null,"截止阀","J41H-16C DN400","介质：蒸汽 耐温：350℃ \n带配对法兰及连接件","个",1,{"$nulls":5},"第四批"]
[12,"S24037387","封闭式电动插板阀","MF941X-2.5","PN0.25MPa DN600，介质：转炉煤气，耐温：150℃，带波纹管，波纹管材质：316L\n带底座、配对法兰、螺栓、螺母及金属缠绕垫片\n带室外防爆电控箱，可实现 PLC 远传控制功能，预留 PLC 接口。","台",1,{"$nulls":5},"第四批"]
[13,"S24037389","电动金属硬密封蝶阀","D943PT-2.5","PN0.25MPa DN600，介质：转炉煤气，耐温：150℃\n带底座、配对法兰、螺栓、螺母及金属缠绕垫片\n带室外防爆电控箱，可实现 PLC 远传控制功能，预留 PLC 接口。","台",1,{"$nulls":5},"第四批"]
[14,"S24037393","闸阀","Z41H-25C","介质：蒸汽 耐温：350℃ 组合/DN400\n带配对法兰及连接件","个",1,{"$nulls":5},"第五批"]
[15,"S24037394","闸阀","Z41H-25C","介质：蒸汽 耐温：350℃ 组合/DN200\n带配对法兰及连接件","个",1,{"$nulls":5},"第五批"]
[16,"S24037395","闸阀","Z41H-25C","介质：蒸汽 耐温：350℃ 组合/DN100\n带配对法兰及连接件","个",1,{"$nulls":5},"第五批"]
[null,"合计",{"$nulls":4},16]
["总价：  佰  拾  万  仟  佰  拾  元整（大写） ",{"$nulls":9},"¥          元"]
["注："]
["    1、单价为含税到厂价，一票结算，税率13%。"]
["    2、报价时请务必注明付款方式。"]
["3、报价文件中须附带报价产品详细技术参数。"]
["报价人（章）：",{"$nulls":8},"2024年  月  日于首钢长钢"]

{"sheet":"B标段补偿器","index":1,"n_rows":19,"n_cols":13,"rows_kept":19,"merged":[[0,0,0,2],[1,0,1,13],[2,0,2,3],[12,1,12,3],[12,9,12,12],[13,0,13,9],[15,0,15,14],[16,0,16,14],[17,0,17,14],[18,0,18,3],[18,9,18,12]],"flags":["formulas_cached_only"]}
["附件3："]
["报 价 货 物 数 量 及 价 目 表"]
["比选编号：长招办询2024-003",{"$nulls":11},"B标段"]
["序号","物料代码","物料名称","规格/型号","技术要求","单位","数量","单价\n（元）","合计（元）","付款方式","交货期","报价货物品牌/厂家","备注"]
[1,"S24037367","横向大拉杆补偿器","介质：蒸汽 耐温：350℃，PN1.6MPa DN400","轴向补偿量：262mm 轴向刚度：17N/mm，波纹管材质：316L，带导流筒，导流筒材质 45MnB","台",1,{"$nulls":5},"第二批"]
[2,"S24037368","无推力套筒补偿器","介质：蒸汽 耐温：350℃ PN1.6MPa DN400","补偿量≥250mm，带防拉断装置，焊接连接，密封材料：柔性石墨环，材质：Q235-B","台",4,{"$nulls":5},"第二批"]
[3,"S24037378","轴向波纹补偿器","2.5TB1800×6-J-820","PN0.25MPa DN1800，介质：高炉煤气，轴向补偿量△x=106mm，轴向刚度：403N/mm，总长 L=820mm，波纹管材质：316L\n接管规格 D1820x10，材料 Q235B","台",1,{"$nulls":5},"第二批"]
[4,"S24037379","轴向波纹补偿器","2.5TB1000×6-J-796","PN0.25MPa DN1000，介质：焦炉煤气，轴向补偿量△x=117mm，轴向刚度：245N/mm，总长 L=796mm，波纹管材质：316L\n接管规格 D1020x8，材料 Q235B","台",1,{"$nulls":5},"第二批"]
[5,"S24037380","轴向波纹补偿器","2.5TB600×8-J-816","PN0.25MPa DN600，介质：转炉煤气，轴向补偿量△x=140mm，轴向刚度：135N/mm，总长 L=816mm，波纹管材质：316L\n接管规格 D630x6，材料 Q235B","台",1,{"$nulls":5},"第二批"]
[null,"S24037381","小拉杆三向波纹补偿器","2.5XHB1000×8-J-1500","PN0.25MPa DN1000，介质：焦炉煤气，轴向补偿量△x=156mm，轴向刚度：184N/mm，横向补偿量△x=72mm，横向刚度：239N/mm，总长 L=1500mm，波纹管材质：316L\n接管规格 D1020x8，材料 Q235B","台",1,{"$nulls":5},"第二批"]
[6,"S24037385","小拉杆三向波纹补偿器","2.5XHB2000×8-J-1500","PN0.25MPa DN2000，介质：高炉煤气，轴向补偿量△x=176mm，轴向刚度：354N/mm，横向补偿量△x=67mm，横向刚度：759N/mm，总长 L=1500mm，波纹管材质：316L\n接管规格 D2020x10，材料 Q235B","台",1,{"$nulls":5},"第四批"]
[8,"S24037382","小拉杆三向波纹补偿器","2.5XHB600×8-J-1500","PN0.25MPa DN600，介质：转炉煤气，轴向补偿量△x=140mm，轴向刚度：135N/mm，横向补偿量△x=107mm，横向刚度：65N/mm，总长 L=1500mm，波纹管材质：316L\n接管规格 D630x6，材料 Q235B","台",1,{"$nulls":5},"第二批"]
[null,"合计",{"$nulls":4},11]
["总价：  佰  拾  万  仟  佰  拾  元整（大写） ",{"$nulls":9},"¥          元"]
["注："]
["    1、单价为含税到厂价，一票结算，税率13%。"]
["    2、报价时请务必注明付款方式。"]
["3、报价文件中须附带报价产品详细技术参数。"]
["报价人（章）：",{"$nulls":8},"2024年  月  日于首钢长钢"]